## Headend
Site Name
Head End & Consoles (Direct runs only - no daisy chaining)
Device | Number Per System | Power Supplies Required
R5KM8PRT - Ethernet Switch |  | 0
R5KMSC - Main System Controller |  | 0
351010 - Responder Network Concentrator |  | 0
351006 - Fiber Optic Adapter Module |  | 0
R5KCONS - VOIP Console
R5KL2KA - L-Net to K-Bus Adapter
R5KMPR36 Power Supplies Required |  | 0
Notes:
It is assumed each R5KCONS is powered either via the R5KMSC or the R5KM8PRT.
It is assumed the uplink ports of the R5KM8PRT are only used to interconnect other R5KM8PRT switches.
It is assumed that each R5KMSC will have an unused POE port for configuring with no downtime.
The R5KL2KA is powered by the L-NET via the R5KMSC. The R5KMSC only supplies power to 4 R5KL2KA units max.
R5KMSC current is calculated with the above assumtions (doesn't match labeling). (2 - .328 + 4 x .130 = 2.192A)
If the number of R5KCONS per system turns red, more R5KM8PRTs or R5KMSCs are needed.
If the number of R5KL2KA per system turns red, more R5KMSCs are needed.
It is assumed 351006 is powered directly from a power supply, disregard the required supplies if powered via POE.

## 1
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 2
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 3
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 4
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 5
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 6
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 7
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 8
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 9
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 10
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 11
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 12
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 13
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 14
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on Y26: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 15
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 16
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 17
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 18
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 19
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## 20
Site Name
R4KANNV2 and R4KMQCV2 | [21 empty] | Cumulative Supply Current | Available Supply Current | Total K-Bus Length Used | Remaining K-Bus Length (Meters)
Run |  | Device Model |  | Cable Length (m) | Number of R4KANNV2s Wired in Series With This R4KANNV2 |  |  | Device Current (mA) RAW |  | Console Cluster Additional Power |  |  |  | Device Current (mA) Staff Reg Effect | Device Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) |  | Power Cable Gauge | Voltage at Node (V) | Will Node Work | [9 empty] | Paging | Zone
[26 empty] | 0 |  |  | Idle | Enhanced | R4KFB1 | Loading | Staff Reg | CLAR4
[26 empty] | 1 | R5KCL546 | 5-bulb 4 Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 2 | R5KCL516 | 5-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 3 | R5KCL506 | 5-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[26 empty] | 4 | CLA246 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[26 empty] | 5 | CLA246w/CLAR46 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[26 empty] | 6 | R5KDC46 | Domeless Controller 4 Audio - 6 total pts. | 21 | 25 | 1 | 0 | 0 | 1
[26 empty] | 7 | R5KDC06 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 8 | R5KDC016 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 9 | R5KDC16D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
[26 empty] | 10 | R5KDC06w/DCRC4 | Domeless Controller Visual - 6 pts with R5KDCRC4 | 21 | 10 | 0 | 0 | 0 | 0
[26 empty] | 11 | R5KDC46w/DCRCS4 | Domeless Controller 4 Audio - 6 total pts with R5KDCRCS4 | 21 | 25 | 1 | 0 | 0 | 1
[22 empty] | (mA) | (mA) | (m) | (m) | 12 | CLA214D | Duty Corridor Light | 21 | 0 | 1 | 1 | 1 | 0
|  | iFill in the data in the yellow cells | [17 empty] | 15.5 |  | 0 | 4650 | 0 | 1524 | 13 | CLA222 | 2-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 4.65A MAX |  |  | 14 | CLA222w/CLAR4 | 2-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 0 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 2.5A Max | 2.5A MAX | 2.5A MAX | 15 | CLA244 | 4-bulb Audio Corridor Light | 21 | 25 | 1 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | Run 1 | Run 2 | Run 3 | 16 | CLA244w/CLAR4 | 4-bulb Audio Corridor Light with CLAR4 | 21 | 25 | 1 | 1 | 1 | 1
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | (mA) | (mA) | (mA) | 17 | CLV122 | 2-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 0 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | 0 | 0 | 0 | 18 | CLV144 | 4-bulb Visual Corridor Light | 21 | 10 | 0 | 1 | 1 | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | CAT5 (24 AWG, 2pr) |  |  |  | OK | OK | OK | 19 | DCA200 | Domeless Controller Audio - 6 pts. | 21 | 25 | 1 | 0 | 0 | 0
Corridor Lights & Domeless Controllers | [25 empty] | 20 | DCA200w/CLAR4 | Domeless Controller Audio - 6 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
Run | Node # | Device Model | Cable Length (m) | Number of Enhanced Stations in room | Number of R4KFB1s in room | Number of R4KFAMs in room | Check if CL is a Zone Light | Device Current (mA) RAW | Additional Current (mA) Enhanced Effect | Additional Current (mA) R4KFB1 Effect | Additional Current (mA) R4KFAM | Additional Current (mA) Zone Effect | Additional Current (mA) Paging Effect | Additional Current (mA) Staff Reg Effect | Additional Current (mA) Loading Effect | Wire Resistance (ohm/m) | Device Current (mA) | Rest of the Run Current (mA) | Power Cable Gauge | Voltage at Node (V) | Will Node Work |  |  Options  |  |  | 21 | DCA200w/OUT4S | Domeless Controller Audio - 6 pts with R4KOUT4S | 21 | 25 | 1 | 0 | 0 | 0
[26 empty] | 22 | DCA200w/OUT4S&CLAR4 | Domeless Controller Audio - 6 pts with R4KOUT4S and CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[24 empty] | FALSE |  | 23 | DCA214D | Duty Domeless Controller | 21 | 0 | 1 | 0 | 0 | 0
i Fill in the data in the yellow cells  | [19 empty] | 15.5 |  |  |  | FALSE |  | 24 | DCA216 | Domeless Controller Audio - 16 pts. | 21 | 25 | 1 | 0 | 0 | 0
1 | [6 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Loading |  |  | 25 | DCA216w/CLAR4 | Domeless Controller Audio -16 pts with CLAR4 | 21 | 25 | 1 | 0 | 0 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 26 | DCV100 | Domeless Controller Visual - 6 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 27 | DCV100w/OUT4R | Domeless Controller Visual - 6 pts with R4KOUT4R | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  |  | 40% |  | 28 | DCV116 | Domeless Controller Visual - 16 pts. | 21 | 10 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 40 |  |  | 29 | R4KANNV2 | Annunciate Panel | 265 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 30 | R4KMQCV2 | Marquee Controller | 300 | 0 | 0 | 0 | 0 | 0
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Wire Gauge Resistance |  |  | 1 | 1
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Standard K-Bus Run |  |  | 2 | 1a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 3 | 1b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT5 (24 AWG, 2pr) |  | 0.084186 | 1a | 1c | [7 empty] | CAT5 (24 AWG, 2pr) | 0.084186
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | CAT6 (23 AWG, 2pr) |  | 0.067913 | 2a | 1d | [7 empty] | CAT6 (23 AWG, 2pr) | 0.067913
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | Remote Power Run |  |  | 3a | 1e | [7 empty] | *CAT5 (24 AWG, 4pr) | 0.042093
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | AWG |  | ohms/m | 1b | 2 | [7 empty] | *CAT6 (23 AWG, 4pr) | 0.033957
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT5 (24 AWG, 4pr) |  | 0.042093 | 2b | 2a | [7 empty] | 12 AWG | 0.01063
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *CAT6 (23 AWG, 4pr) |  | 0.033957 | 3b | 2b | [7 empty] | 14 AWG | 0.016864
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 12 AWG |  | 0.01063 | 1c | 2c | [7 empty] | 16 AWG | 0.026903
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 14 AWG |  | 0.016864 | 2c | 2d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | 16 AWG |  | 0.026903 | 3c | 2e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) |  |  |  | *4pr assumes all 4 pairs will be used for power. Remote power runs require an R4KKBSP for powering K-Bus devices. |  |  | 1d | 3
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2d | 3a
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3d | 3b
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 1e | 3c
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 2e | 3d
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr) | [6 empty] | 3e | 3e
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
[7 empty] | FALSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAT5 (24 AWG, 2pr)
Unit Converter
|  | From |  |  | To
Length |  |  | feet |  | 0 | meters(m)
|  |  | yards |  | 0 | meters(m)
|  |  | meters(m) |  | 0 | feet
|  |  | meters(m) |  | 0 | yards
Current |  |  | amps(A) |  | 0 | milliamps(mA)
|  |  | milliamps(mA) |  | 0 | amps(A)
Audio Paging
Staff Registration
Note on W2: This is the total current consumed by all devices listed on this page.
Note on X2: This is the total current remaining for this power supply.
Note on Y2: This is the length of all K-Bus runs on this sheet.
Note on Z2: This is the total K-Bus length for all sheets within this workbook.
Note on A3: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on C3: Select a model from the drop down list of the cells below.
Note on E3: Head-end Equipment must be run direct to the power supply.
Note on F3: The R4KANNV2 has input and output connections allowing you to wire up to 4 of them in series.
Note on R3: Total current for this device and its options (i.e. audio paging)
Note on T3: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U3: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V3: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 3.5A limit.
Note on X18: 4.65A is Max limit of R5KMPR15
Note on X19: 2.5A is Max limit per R5KMTRM Run
Note on Y19: 2.5A is Max limit per R5KMTRM Run
Note on Z19: 2.5A is Max limit per R5KMTRM Run
Note on X20: This is the leftmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Y20: This is the middle set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on Z20: This is the rightmost set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on X23: OK = Run is properly configured. Page Limit = Run not within 400 feet or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Y23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on Z23: OK = Run is properly configured. Page Limit = Run not within 122 meters or more than 16 nodes. Over 2.5A = Beyond power supply run limit of 2.5A. Over Limit = Beyond power supply 4.65A total limit.
Note on A25: A "Run" is set of power terminals on the R5KMPR15. See "Notes" worksheet for a picture.
Note on B25: A "Node" is a corridor light or domeless controller wired in series with other nodes on a single run.
Note on C25: Select a model from the drop down list of the cells below.
Note on D25: For Corridor Lights, enter the length of the cable from the device to the previous device.
Note on E25: Enhanced stations have lighting control capabilities. R5KPS1EA R5KPD2EA R4K13VA R4K16LV R4K23VA R4K25LV R4K17V
Note on F25: R4KFB1 Each Feature bed interface draws 75mA. They are limited to 2 per room.
Note on G25: Each R4KFAM draws 30mA. They are limited to 6 per corridor light or 16 per 16 pt controller.
Note on H25: Because zone lights are on more often, this check-box will double the loading percentage for this device.
Note on R25: Total current for this device and its options (i.e. audio paging)
Note on S25: Loading current for the rest of the device on the power run.
Note on T25: Select the gauge of power cable used. 2 pair CAT-5 is default.
Note on U25: This voltage can be verified by measuring the voltage at the device with a digital volt meter.
Note on V25: This will give an indication whether or not this device will work. "No" means the device will not have enough voltage. "Over Limit" means the power supply is over its 4.65A limit.
Note on X27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y27: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on Y28: The Audio Paging checkbox calculates additional current drawn by each CL/DC. Each PA-25 should be on a separate supply.
Note on X29: Loading refers to the maximum percentage of calls estimated at the busiest point.

## Estimate
Device Model |  | Number Per System | Typ Power Draw (A) | Total Draw Per System |  | Enter Cost | Subtotal
Stations
HSS400 | High Security Bed Station |  | 0.01
HSS401 | High Security Staff Station |  | 0.008
HSS433 | High Security Push Button Station |  | 0.015
R4K11V | Single Bed Visual Station |  | 0.002
R4K12A | Single Bed Audio Station |  | 0.005
R4K12AHZ | Horizontal Single Bed Audio Station |  | 0.005
R4K13VA | Single Bed Enhanced Audio Station |  | 0.025
R4K17V | SLIM Single Bed Enhanced Audio St |  | 0.025
R4K13VAHZ | Horiz. Single Bed Enhanced Audio Stn |  | 0.025
R4K14SA | Staff Assist Bed Station |  | 0.007
R4K15V | SLIM 1/4" Jack Button Station |  | 0.007
R4K16LV | Single Bed Enhanced Visual Station |  | 0.015
R4K21V | Dual Bed Visual Station |  | 0.004
R4K22A | Dual Bed Audio Station |  | 0.007
R4K2JACK | SLIM Dual 1/4" Jack Audio Station |  | 0.007
R4K23VA | Dual Bed Enhanced Audio Station |  | 0.03
R4KCB10 | Code Station |  | 0.007
R4KCB12 | Code Station w/Timer |  | 0.017
R4KCB13 | SLIM Code Station w/Timer |  | 0.017
R4KCNCL | Cancel Station |  | 0.002
R4KDLC2 | Dual Lighting Controller |  | 0.023
R4KDY | Duty Station |  | 0.012
R4KDTY2 | SLIM Duty Station |  | 0.012
R4KESR | Emergency Staff Reg. Station |  | 0.007
R4KSAR | SLIM Dual Push w-Staff Reg Station |  | 0.007
R4KFAM | Fire/Auxiliary Module |  | 0.03
R4KFB1 | Feature Bed Interface |  | 0.075
R4KMST | Marquee Speaker |  | 0.005
R4KPB11 | Push For Help Station |  | 0.004
R4KPB12 | SLIM Push For Help Station |  | 0.004
R4KPB22 | Dual Push Button Station |  | 0.017
R4KPB23 | SLIM Dual Push Button Station |  | 0.017
R4KPB44 | Four Button Station |  | 0.014
R4KPC10 | Pull Cord Station |  | 0.002
R4KPC11 | SLIM Pull Cord Station |  | 0.002
R4KRA1 | Residence Assist Station |  | 0.007
R4KSLC1 | Single Lighting Controller |  | 0.013
R4KSR1 | Staff Registration Station |  | 0.002
R4KSS | Staff Station |  | 0.005
R4KTVR1 | Digital TV Isolation Module |  | 0.015
R5KPS1V | Responder 5k Single Pat Visual |  | 0.003
R5KPB4 | Responder 5k Four Button St |  | 0.011
R5KPD2EA | Responder 5k Enhanced Dual Audio Patient Station |  | 0.015
R5KPS1EA | Responder 5k Enhanced Single Audio Patient Station |  | 0.011
R5KPD2A | Responder 5k Dual Audio Patient Station |  | 0.01
R5KPS1A | Responder 5k Single Audio Patient Station |  | 0.008
R5KSSTF | Responder 5k Staff Station |  | 0.016
R5KSDTY | Responder 5k Duty Station |  | 0.027
R5KPS1LCA | Responder 5k Single Audio Patient Station with Button and Light Control |  | 0.031
Corridor Light/Domeless Controllers
DCV100 | 6 Point Visual Domeless Controller |  | 0.012 |  | Loading
R4KOUT4R | Visual Output Controller |  | 0.032
DCV116 | 16 Point Domeless Controller |  | 0.012
CLV122 | 2 Bulb Visual Corridor Light |  | 0.012
CLV144 | 4 Bulb Visual Corridor Light |  | 0.012
DCA200 | 6 Point Audio Domeless Controller |  | 0.038 |  | 60
R4KOUT4S | Audio Output Controller |  | 0.021 |  | 60%
DCA216 | 6 Point Audio Domeless Controller |  | 0.038
CLA214D | Duty Corridor Light |  | 0.058
DCA214D | Duty Domeless Controller |  | 0.058
CLA222 | 2 Bulb Audio Corridor Light |  | 0.038
CLA244 | 4 Bulb Audio Corridor Light |  | 0.038
CLAR4 | Corridor Light Audio Relay Add-on |  | 0.032
CLA246 | 4 Bulb Audio Corridor Light |  | 0.038
CLAR46 | Corridor Light Audio Relay Add-on |  | 0.032
R5KCL546 | CL 4 audio 6 stations |  | 0.058
R5KDC46 | Domeless 4 audio 6 stations |  | 0.038
R5KCL516 | CL 1 audio 6 stations |  | 0.038
R5KCL506 | CL 6 stations |  | 0.036
R5KDC06 | Domeless 6 stations |  | 0.016
R5KDC016 | Domeless 16 stations |  | 0.017
R5KDC16D | Domeless Duty 1 Audio 6 stations |  | 0.058
R5KDCRC4 | Relay Output Controller |  | 0.032
R5KDCRC4 | Solid State Relay Output Controller |  | 0.021
Consoles and Annunciators
R4KANNV2 | Annunciator Panel |  | 0.375
R4KMQCV2 | Marquee Controller |  | 0.3
R5KCONS | VOIP Console |  | 0.328
Network and Control Equipment
R4KPA25 | 25W Paging Amp |  | 2.5
R5KMSC | Main System Controller |  | 2.192
R5KL2KA | L-Net to K-Bus Adapter |  | 0.13
351010 | Responder Network Concentrator |  | 0.3
R5KM8PRT | R5K 8 Port POE Ethernet Switch |  | 2.4
351006 | Fiber Optic Adapter Module |  | 0.075
Device Model |  | Number Per System | Power Draw (A) | Total Draw Per System
Stations
Grand Total (15V) |  |  |  | 0
Grand Total (36V) |  |  |  | 0
R4KPR400 Power Supplies Required |  |  |  | 0
R5KMPR15 Power Supplies Required |  |  |  | 0
R5KMPR36 Power Supplies Required |  |  |  | 0
Notes:
It is assumed the R5KCONS is powered either via the R5KMSC or the R5KM8PRT.
It is assumed the uplink ports of the R5KM8PRT are only used to interconnect other R5KM8PRT switches.
It is assumed that each R5KMSC will have an unused POE port for configuring with no downtime.
The R5KL2KA is powered by the L-NET via the R5KMSC. The R5KMSC only supplies power to 4 R5KL2KA units max. | [5 empty] | Total | 0
R5KMSC current is calculated with the above assumtions (doesn't match labeling). (2 - .328 + 4 x .130 = 2.192A)
If the number of R5KCONS per system turns red, more R5KM8PRTs or R5KMSCs are needed.
If the number of R5KL2KA per system turns red, more R5KMSCs are needed.
It is assumed 351006 is powered directly from a power supply, disregard the required supplies if powered via POE.
Note on F53: Loading refers to the maximum percentage of calls estimated at the busiest point.

## Notes
Responder 5000 Power Calculation Workbook
For further notes please refer to the manual
KI-2907 - Responder 5000 Installation Guide
This workbook should be used to assist you in planning the wiring of a Responder 5000 installation.
Each worksheet (yellow tabs 1-20) helps you to determine the number of devices that can be powered by a single R5KMPR15 Power Supply based on device selection, cable length, and layout variables. Please keep in mind that the entire workbook including all tabs accounts for a complete Responder 5000 system with multiple R5KMSCs, R5KL2Ks and multiple R5KMPR15s. Certain, very large, configurations will require multiple instances of the workbook to account for all devices of the Nurse Call System.
In addition, the utility provides a "pre-sale" power supply estimate worksheet. This can be used to help you estimate the number of power supplies a site will need. The calculations are conservative to reserve room for additions in the future when detailed configurations are completed.
The spreadsheets assume runs 1, 2, and 3 are corridor lights runs wired in series from three (3) separate R5KMTRM runs. For parallel runs (when one (1) output of the supply powers two (2) R5KMTRMs runs), select 1-1e, 2-2e or 3-3e. See above image for sample runs. These runs are calculated as if they were parallel runs on an R5KMTRM. R4KANNV2s and R4KMQCV2s are tracked separately from CLs but included on the same power supply. Attention should be paid to the total current display for each run to stay within the power supply unit limits. | Single power supply example
Calculation formulas